## Start Sequence
State | Tested Action | Action | Effects | Comments
The process is in start state Intake air damper status/closed FS-114 = 1 Intake air damper status/Open FS-115 = 0 Exhaust air damper status/closed FS-213 = 1 Exhaust air damper status/open FS-214 = 0 Smoke extraction damper status/closed FS-315 = 1 Smoke extraction damper status/open FS-314 = 0 Intake air fan status FS-113 = 0 Exhaust air fan status FS-212 = 0 Smoke extraction fan status FS-313 = 0 Emergency Button HZ-413 = 1 Reset/Stop PS-411 = 0 Fire Alarm Outside QE-116 = 0 Fire Alarm Inside QE-316 = 1 Fire lock = 0 | Automated Air circulation and room temperature control system | The process is started pressing the start button PS-410 momentarily I6.0 > 1, 0 | The intake dampener open control FCS-110 turns on Q0.1 > 1 The exhaust dampener open control FCS-210 turns on Q0.3 > 1
Emergency Button HZ-413 = 1 Reset/Stop PS-411 = 0 Fire Alarm Outside QE-116 = 0 Fire Alarm Inside QE-316 = 1 Fire lock = 0 | The Intake and Exhaust dampers get the open status and turn off the open control | The dampeners reach the open status Intake Damper status/open FS-115 I0.1 > 1 Intake damper status/closed FS-114 I0.5 > 0 Exhaust Damper status/open FS-214 I0.0 > 1 Exhaust damper status/closed FS-213 I0.4 > 0 | The intake dampener open control FCS-110 turns off Q0.1 > 0 The Exhaust dampener open control FCS-210 turns off Q0.3 > 0
| Dampeners dont reach the open status within 15s | Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 0 Exhaust Damper status/open FS-214 I0.0 > 0 Exhaust damper status/closed FS-213 I0.4 > 0 or Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 1 Exhaust Damper status/open FS-214 I0.0 > 0 Exhaust damper status/closed FS-213 I0.4 > 1 | Gives an alarm Intake damper alarm > 1 Exhaust damper alarm > 1 Continues the process
Emergency Button HZ-413 = 1 Reset/Stop PS-411 = 0 Fire Alarm Outside QE-116 = 0 Fire Alarm Inside QE-316 = 1 Fire lock = 0 | Turning on the fans | Intake Damper status/open FS-115 I0.1 > 1 Intake damper status/closed FS-114 I0.5 > 0 Exhaust Damper status/open FS-214 I0.0 > 1 Exhaust damper status/closed FS-213 I0.4 > 0 | The Fan control FC is turned on M20.0 > 1
| Fans dont reach the control time of 15s | After the fan control FC is turned on if 15s pass intake air fan status FS-113 dosen turn off I6.1 > 0 Exhaust air fan status FS-212 dosent turn off I6.4 > 0 | Gives an alarm Fan alarm > 1 Iniates the stop sequence
| The fan status is checked after which the process is in the run state | intake air fan status FS-113 I6.1 > 1 Exhaust air fan status FS-212 I6.4 > 1
| Stop Button is pressed | The Process is stopped by pressing the stop button PS-411 momentarily I6.3 > 1, 0 | The fan control FC is turned off M20.0 > 0
| If the fan control time of 15s is not reached the process gives an alarm is given | After the fan control FC is turned on if 15s pass intake air fan status FS-113 dosent turn on I6.1 > 1 Exhaust air fan status FS-212 dosen't turn on I6.4 > 1 | Gives an alarm Fan alarm > 1 Continues the stop sequence
| The fan close status is checked and the dampers start to close if in alarm state the process is also stopped | intake air fan status FS-113 I6.1 > 0 Exhaust air fan status FS-212 I6.4 > 0 if alarm intake air fan status FS-113 I6.1 > 1 Exhaust air fan status FS-212 I6.4 > 1 | The intake dampener close control FCS-111 turns on Q0.2 > 1 The exhaust dampener close control FCS-211 turns on Q0.4 > 1
| Dampeners dont reach the close status within 15s | Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 0 Exhaust Damper status/open FS-214 I0.0 > 0 Exhaust damper status/closed FS-213 I0.4 > 0 or Intake Damper status/open FS-115 I0.1 > 1 Intake damper status/closed FS-114 I0.5 > 0 Exhaust Damper status/open FS-214 I0.0 > 1 Exhaust damper status/closed FS-213 I0.4 > 0 | The intake dampener close control FCS-111 turns off Q0.2 > 0 The exhaust dampener close control FCS-211 turns off Q0.4 > 0 the process is stopped and alarm is given Intake damper alarm > 1 Exhaust damper alarm > 1
| The dampers reach the close status and the process is stopped | Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 1 Exhaust Damper status/open FS-214 I0.0 > 0 Exhaust damper status/closed FS-213 I0.4 > 1 | The intake dampener close control FCS-111 turns off Q0.2 > 0 The exhaust dampener close control FCS-211 turns off Q0.4 > 0
| A fire is detected | Fire Alarm In vent QE-116 > 1 or inside the appartment QE-316 > 0 | Smoke extraction damper control open FCS-311 is turned on Q0.6 > 1 Smoke extraction fan control FCS-310 is turned on Q0.5 > 1
| Checking that the smoke exraction has been turned on after which the stop sequence is initialized closing the intake and exhaust | Smoke fan status FS-313 I6.2 > 1 Smoke damper status/open FS-314 I0.2 > 1 Smoke damper status/closed FS-315 I0.6 > 0 | Start the stop sequence
| If control time for the smoke damper or fan is not reached give an alarm | Smoke fan status FS-313 I6.2 > 0 Smoke damper status/open FS-314 I0.2 > 0 Smoke damper status/closed FS-315 I0.6 > 0 or Smoke damper status/open FS-314 I0.2 > 0 Smoke damper status/closed FS-315 I0.6 > 1 | Give a alarm Smoke damper alarm > 1 Smoke fan alarm > 1
| Holding the stop/reset button for 10s | Starts the reset sequence by pressing the stop/reset button PS-411 for 10s I6.3 > 1, 0 Starts to close the fans if they are on if intake air fan status FS-113 I6.1 > 1 or Exhaust air fan status FS-212 I6.4 > 1 | fan control FC turn off M20.0 > 0
| After the fans have been turned off start closing intake damper if open | intake air fan status FS-113 I6.1 > 0 Exhaust air fan status FS-212 I6.4 > 0 Intake Damper status/open FS-115 I0.1 > 1 Intake damper status/closed FS-114 I0.5 > 0 | The intake dampener close control FCS-111 turns on Q0.2 > 1
| after the intake damper has closed start closing the exhaust damper if open | Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 1 Exhaust Damper status/open FS-214 I0.0 > 1 Exhaust damper status/closed FS-213 I0.4 > 0 | The intake dampener close control FCS-111 turns on Q0.2 > 0 The exhaust dampener close control FCS-211 turns on Q0.4 > 1
| After the dampers reach the closed status stop the closing control | Intake Damper status/open FS-115 I0.1 > 0 Intake damper status/closed FS-114 I0.5 > 1 Exhaust Damper status/open FS-214 I0.0 > 0 Exhaust damper status/closed FS-213 I0.4 > 1 | The exhaust dampener close control FCS-211 turns on Q0.4 > 0
| If the smoke extraction fan is turned on turn it off | Smoke extraction fan status FS-313 I6.2 > 1 | Smoke extraction fan control FCS-310 is turned off Q0.5 > 0
| After the smoke extraction fan is turned off if the smoke extraction damper is not closed. | Smoke extraction fan status FS-313 I6.2 > 0 Smoke damper status/open FS-314 I0.2 > 1 Smoke damper status/closed FS-315 I0.6 > 0 | Smoke damper control close FCS-312 Turns on Q0.7 > 1
| After the smoke damper is closed the reset sequence is completed and resets all the ongoing alarms | Smoke damper status/open FS-314 I0.2 > 0 Smoke damper status/closed FS-315 I0.6 > 1 | Smoke damper control close FCS-312 Turns off Q0.7 > 0 Fire lock > 0 Alarm > 0 Emergency > 0
| If emergency button is pressed Dosent affect the smoke extraction fan or damper | Emergency button HZ-413 > 0 | Emergency > 1 Starts the stop sequence
Note on F3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Testing this commenting Reply: ok Reply: all good
Note on F4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: alarms did not work. Reply: alarms didnt work in HMI but worked in tiaportal program
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: alarms did not work Reply: didnt work in HMI, worked in tiaportal
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: alarms did not work Reply: did work in program, didnt work in HMI
Note on F11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: worked in tiaportal, not in HMI
Note on F13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: all good Reply: ok
Note on F16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: works in tiaportal for opening seq. Reply: works in tiaportal for closing seq.
Note on F17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: all good Reply: ok
Note on F18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok. Reply: all good
Note on F20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: all good
Note on F21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good
Note on F24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: ok Reply: all good